## Machine list Plant_A
No. | Phase | Plant | No. of MC | Room | Name Machine | Control | HMI | Data Monitor |  |  | Data record | Number of Inputs | Number of word | Data type | Collection method | Device discription | Remark | I/O Sum | Word Sum | Collect Data | Collect Data
[8 empty] | Operation status | status | Value
1 | 3 | A | 4 | Prepare for fry | High-Cook New ( Front ) | PLC FX-3U64 MT | GOT2000 (GT2508-VTBD) | Temperature |  | 135 deg.C | deg.C |  | 1 | Word | PLC Link |  | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module |  | 200 | Box Main 2 ( Plant A )
[8 empty] | Outlet temp |  | 138 deg.C | deg.C |  | 1 | Word
[8 empty] | Cooking time |  | 2 Min | time |  | 1 | Word
[8 empty] | Oil supply level | High,OK,Low |  | Alert Low,High |  | 1 | Word
[8 empty] | Flat top Carrying time |  | 2.3 Min | time |  | 1 | Word
[8 empty] | In-peration/Home |  |  | Operation time |  | 1 | Bit
[8 empty] | Auto running |  |  | Operation time |  | 1 | Bit
[8 empty] | Stopping |  |  | Operation time |  | 1 | Bit
[8 empty] | Emergency stop |  |  | stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 41
2 | 3 | A | 1 | Prepare for fry | Sunmax | PLC FX-3U**** | GOT2000 **** | Temperature1 | High,OK,Low | 100 deg C | temp |  | 1 | Word | PLC Link | DIGICON DR-S8N | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module |  | 50 | Box Main 2 ( Plant A )
[8 empty] | Temperature2 | High,OK,Low | 100 deg C | temp |  | 1 | Word |  | DIGICON DR-S8N
[8 empty] | Temperature3 | High,OK,Low | 100 deg C | temp |  | 1 | Word |  | DIGICON DR-S8N
[8 empty] | Frying Temp1 | High,OK,Low | 100 deg C | temp |  | 1 | Word |  | OMRON E5CC
[8 empty] | Frying Temp2 | High,OK,Low | 100 deg C | temp |  | 1 | Word |  | OMRON E5CC
[8 empty] | Pump1 Revolution |  | 50 Hz |  |  | 1 | Word
[8 empty] | Pump2 Revolution |  | 50 Hz |  |  | 1 | Word
[8 empty] | Main C/V |  | 50 Hz |  |  | 1 | Bit
[8 empty] | Receive C/V |  | 50 Hz |  |  | 1 | Bit
[8 empty] | Pump1 | On,Off |  |  |  | 1 | Bit
[8 empty] | Pump2 | On,Off |  |  |  | 1 | Bit
[8 empty] | Main C/V | On,Off |  |  |  | 1 | Bit
[8 empty] | Receive C/V | On,Off |  |  |  | 1 | Bit
[8 empty] | Heater | On,Off |  |  |  | 1 | Bit
[8 empty] | Fan1 | On,Off |  |  |  | 1 | Bit
[8 empty] | Fan2 | On,Off |  |  |  | 1 | Bit
[8 empty] | Filter | On,Off |  |  |  | 1 | Bit
[8 empty] | Scraper | On,Off |  |  |  | 1 | Bit
[8 empty] | Lift Up | On,Off |  |  |  | 1 | Bit
[8 empty] | Lift Down | On,Off |  |  |  | 1 | Bit
[8 empty] | In-peration/Home |  |  | Operation time |  | 1 | Bit
[8 empty] | Auto running |  |  | Operation time |  | 1 | Bit
[8 empty] | Stopping |  |  | Operation time |  | 1 | Bit
[8 empty] | Emergency stop |  |  | stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 26 | Bit
3 | 3 | A | 1 | Prepare for fry | KOPPEN FRYER | Hard wire | Don't Have | Frying Temp 1 | High,OK,Low |  |  | 3 |  | Digital Input | I/O Link | OMRON E5CC | Add relay for tab signal,Re layout | 31 |  | Box Main 2 ( Plant A ) | Slave Box 2-1
[8 empty] | Frying Temp 2 | High,OK,Low |  |  | 3 |  |  |  | OMRON E5CC
[8 empty] | Frying Temp 3 | High,OK,Low |  |  | 3 |  |  |  | OMRON E5CC
[8 empty] | Receive | On,Off |  |  | 1
[8 empty] | Main C/V | On,Off |  |  | 1
[8 empty] | Pump 1 | On,Off |  |  | 1
[8 empty] | Pump 2 | On,Off |  |  | 1
[8 empty] | Heaten | On,Off |  |  | 1
[8 empty] | Infeed C/V | On,Off |  |  | 1
[8 empty] | Bottom | On,Off |  |  | 1
[8 empty] | Blower | On,Off |  |  | 1
[8 empty] | Receive C/V INV ALARM | On,Off |  |  | 1
[8 empty] | MAIN C/V INV ALARM | On,Off |  |  | 1
[8 empty] | PUMP 1 INV ALARM | On,Off |  |  | 1
[8 empty] | PUMP 2 INV ALARM | On,Off |  |  | 1
[8 empty] | LIFT 1 OVERLOAD | On,Off |  |  | 1
[8 empty] | LIFT 2 OVERLOAD | On,Off |  |  | 1
[8 empty] | SEFETY SWITCH ON | On,Off |  |  | 1
[8 empty] | INFEED C/V INV ALARM | On,Off |  |  | 1
[8 empty] | UPPER C/V INV ALARM | On,Off |  |  | 1
[8 empty] | BOTTOM C/V INV ALARM | On,Off |  |  | 1
[8 empty] | BLOWER INV ALARM | On,Off |  |  | 1
[8 empty] | HIGH TEMP ALARM | On,Off |  |  | 1
[8 empty] | LOW TEMP ALARM | On,Off |  |  | 1
[8 empty] | Emergency stop | On,Off |  |  | 1
4 | 3 | A | 1 | Prepare for fry | Steam cooker | Hard wire | Don't Have | Temperature 1 | High,OK,Low |  |  | 3 |  | Digital Input | I/O Link | TOHO TTM-I4N ( Output I/O ) | Add relay for tab signal,Re layout | 18 |  | Box Main 2 ( Plant A ) | Slave Box 2-2
[8 empty] | Temperature 2 | High,OK,Low |  |  | 3 |  |  |  | TOHO TTM-I4N ( Output I/O )
[8 empty] | Temperature 3 | High,OK,Low |  |  | 3 |  |  |  | TOHO TTM-I4N ( Output I/O )
[8 empty] | Conveyor | On,Off |  |  | 1
[8 empty] | Stream SV1 | On,Off |  |  | 1
[8 empty] | Stream SV2 | On,Off |  |  | 1
[8 empty] | Stream SV3 | On,Off |  |  | 1
[8 empty] | Stream SV4 | On,Off |  |  | 1
[8 empty] | Lift UP | On,Off |  |  | 1
[8 empty] | Lift Down | On,Off |  |  | 1
[8 empty] | Overload | On,Off |  |  | 1
[8 empty] | In-peration/Home | On,Off |  |  | 1
5 | 1 | A | 1 | Clean room | Spiral No.2 | Hard wire | Don't Have | Operation | ON,OFF | - | In-operation time | 1 | - | Diital Input | I/O Link |  | Re layout for tab signal | 28 |  | Box Main 3 ( Plant A )
[8 empty] | Liquid SV. | ON,OFF |  | - | 1
[8 empty] | Defrost SV. | ON,OFF |  | - | 1
[8 empty] | Lighting | ON,OFF |  | - | 1
[8 empty] | Machine Alarm | ON,OFF |  | stopping Time | 1
[8 empty] | Room temp high,low alarm | ON,OFF |  | number of times high,Low | 2
[8 empty] | Emergency stop | ON,OFF |  | stopping Time | 1
[8 empty] | Buzzer | ON,OFF |  | - | 1
[8 empty] | Conveyor | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 1 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 2 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 3 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 4 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 5 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 6 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | Water Pump | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | Freezing Temperature |  |  | - |  |  |  |  | TTM-004W-R-A ( Model Relay)
[8 empty] | Counter Unit | INP_A ON,INP_B ON,Reset |  | number of Counter | 3 |  |  |  | Kubler CODIX
6 | 1 | A | 1 | Clean room | Spiral No.3 | Hard wire | Don't Have | Operation | ON,OFF | - | In-operation time | 1 | - | Diital Input | I/O Link |  | Re layout for tab signal | 28 |  | Box Main 3 ( Plant A )
[8 empty] | Liquid SV. | ON,OFF |  | - | 1
[8 empty] | Defrost SV. | ON,OFF |  | - | 1
[8 empty] | Lighting | ON,OFF |  | - | 1
[8 empty] | Machine Alarm | ON,OFF |  | stopping Time | 1
[8 empty] | Room temp high,low alarm | ON,OFF |  | number of times high,Low | 2
[8 empty] | Emergency stop | ON,OFF |  | stopping Time | 1
[8 empty] | Buzzer | ON,OFF |  | - | 1
[8 empty] | Conveyor | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 1 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 2 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 3 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 4 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 5 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | FAN 6 | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | Water Pump | ON,OFF,Overload |  | number of times high,Low | 2
[8 empty] | Freezing Temperature | - |  | - |  |  |  |  | TTM-004W-R-A ( Model Relay)
[8 empty] | Counter Unit | INP_A ON,INP_B ON,Reset |  | number of Counter | 3 |  |  |  | Kubler CODIX
7 | 1 | A | 1 | Clean room | Spiral No.6 | PLC ( Q03UDV ) | GOT2000(GT2510-VTBD) | Room temp |  | -32.3 deg.C | deg.C |  | 2 | Word | PLC Link |  | Add module QJ71EN71-100 |  | 50 | Box Main 3 ( Plant A )
[8 empty] | Freezer pass time |  | 43.0 min | time |  | 2 | Word
[8 empty] | Cooling pass time |  | 38.1 min | time |  | 2 | Word
[8 empty] | Fan speed select |  | High,Mid,Low | - |  | 1 | Bit
[8 empty] | Status massage |  | Cooling | - |  | 1 | Word
[8 empty] | CIP Select |  | Light washing,Full washing,Feeding Finish | - |  | 1 | Word
[8 empty] | Inlet balance fan |  | 50.00 Hz |  |  | 2 | Word
[8 empty] | In-peration |  | - | Operation time |  | 1 | Bit
[8 empty] | Auto running |  | - | Operation time |  | 1 | Bit
[8 empty] | Stopping |  | - | stopping Time |  | 1 | Bit
[8 empty] | Emergency stop |  | - | Stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 35
8 | 1 | A | 1 | Clean room | Spiral No.7 | PLC ( Q03UDV ) | GOT2000(GT2510-VTBD) | Room temp |  | -32.3 deg.C | deg.C |  | 2 | Word | PLC Link |  | Add module QJ71EN71-100 |  | 50 | Box Main 3 ( Plant A )
[8 empty] | Freezer pass time |  | 43.0 min | time |  | 2 | Word
[8 empty] | Cooling pass time |  | 38.1 min | time |  | 2 | Word
[8 empty] | Fan speed select |  | High,Mid,Low | - |  | 1 | Bit
[8 empty] | Status massage |  | Cooling | - |  | 1 | Word
[8 empty] | CIP Select |  | Light washing,Full washing,Feeding Finish | - |  | 1 | Word
[8 empty] | Inlet balance fan |  | 50.00 Hz |  |  | 2 | Word
[8 empty] | In-peration |  |  | Operation time |  | 1 | Bit
[8 empty] | Auto running |  |  | Operation time |  | 1 | Bit
[8 empty] | Stopping |  |  | stopping Time |  | 1 | Bit
[8 empty] | Emergency stop |  |  | Stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 35
9 | 1 | A | 3 | Clean room | Polystar | PLC Fuji ( NP1PU-048E ) | GOT2000 | Model Production |  | B0 22 |  |  | 1 |  | HMI Link ( RS485 or Modbus TCP), PLC Link |  |  |  | 50 | Box Main 4 ( Plant A )
[8 empty] | Bag length |  | 310 |  |  | 1
[8 empty] | Push position |  | 160 |  |  | 1
[8 empty] | Production s |  | 0 |  |  | 1 | Word
[8 empty] | End sealer |  | -12 |  |  | 1 | Word
[8 empty] | Film tension |  | 0 |  |  | 1 | Word
[8 empty] | Wrapping Speed |  | 40 rpm |  |  | 1 | Word
[8 empty] | Push Position |  | 160 mm |  |  | 1 | Word
[8 empty] | Regi-mark Position |  | -0.8 mm |  |  | 1 | Word
[8 empty] | In-peration |  |  | Operation time |  | 1 | Bit
[8 empty] | Auto running |  |  | Operation time |  | 1 | Bit
[8 empty] | Stopping |  |  | Operation time |  | 1 | Bit
[8 empty] | Emergency stop |  |  | stopping Time |  | 1 | Bit
[8 empty] | Alarm |  |  | Stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 36
14

## Machine list Plant_B
No. | Phase | Plant | No. of MC | Room | Name Machine | Control | HMI | Data Monitor |  |  | Data record | Number of Inputs | Number of word | Data type | Collection method | Device discription | Remark | I/O Sum | Word Sum | Collect Data
[8 empty] | Operation status | status | Value
1 | 4 | B | 1 | Fry Fry | Fryer 1 | FX3U-48M | GOT2000 GT2105-QTBDS | Temperature |  | 135 deg.C | deg.C |  | 1 | Word | PLC Link | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module |  |  | Box Main 2 ( Plant B )
[8 empty] | Outlet temp |  | 138 deg.C | deg.C |  | 1 | Word
[8 empty] | Cooking time |  | 2 Min | time |  | 1 | Word
[8 empty] | Oil supply level | High,OK,Low |  | Alert Low,High |  | 1 | Word
[8 empty] | Flat top Carrying time |  | 2.3 Min | time |  | 1 | Word
[8 empty] | In-peration/Home |  |  | Operation time |  | 1 | Bit
[8 empty] | Auto running |  |  | Operation time |  | 1 | Bit
[8 empty] | Stopping |  |  | Operation time |  | 1 | Bit
[8 empty] | Emergency stop |  |  | stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 41
2 | 4 | B | 1 | Fry Fry | Fryer 2 | FX3U-48M | GOT2000 GT2105-QTBDS | Temperature |  | 135 deg.C | deg.C |  | 1 | Word | PLC Link | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module |  |  | Box Main 2 ( Plant B )
[8 empty] | Outlet temp |  | 138 deg.C | deg.C |  | 1 | Word
[8 empty] | Cooking time |  | 2 Min | time |  | 1 | Word
[8 empty] | Oil supply level | High,OK,Low |  | Alert Low,High |  | 1 | Word
[8 empty] | Flat top Carrying time |  | 2.3 Min | time |  | 1 | Word
[8 empty] | In-peration/Home |  |  | Operation time |  | 1 | Bit
[8 empty] | Auto running |  |  | Operation time |  | 1 | Bit
[8 empty] | Stopping |  |  | Operation time |  | 1 | Bit
[8 empty] | Emergency stop |  |  | stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 41
3 | 4 | B | 1 | Fry Fry | KOPPEN FRYER | Hard wire | Don't Have | Frying Temp 1 | High,OK,Low |  |  | 3 |  | Digital Input | I/O Link | OMRON E5CC | Add relay for tab signal,Re layout | 31 |  | Box Main 2 ( Plant B )
[8 empty] | Frying Temp 2 | High,OK,Low |  |  | 3 |  |  |  | OMRON E5CC
[8 empty] | Frying Temp 3 | High,OK,Low |  |  | 3 |  |  |  | OMRON E5CC
[8 empty] | Receive | On,Off |  |  | 1
[8 empty] | Main C/V | On,Off |  |  | 1
[8 empty] | Pump 1 | On,Off |  |  | 1
[8 empty] | Pump 2 | On,Off |  |  | 1
[8 empty] | Heaten | On,Off |  |  | 1
[8 empty] | Infeed C/V | On,Off |  |  | 1
[8 empty] | Bottom | On,Off |  |  | 1
[8 empty] | Blower | On,Off |  |  | 1
[8 empty] | Receive C/V INV ALARM | On,Off |  |  | 1
[8 empty] | MAIN C/V INV ALARM | On,Off |  |  | 1
[8 empty] | PUMP 1 INV ALARM | On,Off |  |  | 1
[8 empty] | PUMP 2 INV ALARM | On,Off |  |  | 1
[8 empty] | LIFT 1 OVERLOAD | On,Off |  |  | 1
[8 empty] | LIFT 2 OVERLOAD | On,Off |  |  | 1
[8 empty] | SEFETY SWITCH ON | On,Off |  |  | 1
[8 empty] | INFEED C/V INV ALARM | On,Off |  |  | 1
[8 empty] | UPPER C/V INV ALARM | On,Off |  |  | 1
[8 empty] | BOTTOM C/V INV ALARM | On,Off |  |  | 1
[8 empty] | BLOWER INV ALARM | On,Off |  |  | 1
[8 empty] | HIGH TEMP ALARM | On,Off |  |  | 1
[8 empty] | LOW TEMP ALARM | On,Off |  |  | 1
[8 empty] | Emergency stop | On,Off |  |  | 1
4 | 4 | B | 1 | Fry Fry | Stream Oven 4 | FX3U-64MT | Proface | Auto running | On,Off |  | Operation time | 1 |  | Digital Input | PLC Link |  | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module | 3 |  | Box Main 2 ( Plant B )
[8 empty] | Stop | On,Off |  | stop Time | 1
[8 empty] | Emergency stop | On,Off |  | stop Time | 1
5 | 4 | B | 1 | Clean room | Spiral No.4 | FX3U-128MT | GOT1000 | Room temp | - | -32.3 deg.C | deg.C |  | 2 | Word | PLC Link |  | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module |  | 50 | Box Main 3 ( Plant B )
[8 empty] | Freezer pass time | - | 43.0 min | time |  | 2 | Word
[8 empty] | Cooling pass time | - | 38.1 min | time |  | 2 | Word
[8 empty] | Fan speed select | - | High,Mid,Low | - |  | 1 | Bit
[8 empty] | Status massage | - | Cooling | - |  | 1 | Word
[8 empty] | CIP Select | - | Light washing,Full washing,Feeding Finish | - |  | 1 | Word
[8 empty] | Inlet balance fan | - | 50.00 Hz |  |  | 2 | Word
[8 empty] | In-peration | - | - | Operation time |  | 1 | Bit
[8 empty] | Auto running | - | - | Operation time |  | 1 | Bit
[8 empty] | Stopping | - | - | stopping Time |  | 1 | Bit
[8 empty] | Emergency stop | - | - | Stopping Time |  | 1 | Bit
[8 empty] | Reserve | - |  |  |  | 35
6 | 4 | B | 1 | Clean room | Spiral No.5 | FX3U-128MT | GOT2000 | Room temp |  | -32.3 deg.C | deg.C |  | 2 | Word | PLC Link |  | Add module FX3U-ENET-ADP + Cable Expiantion 0.5M, Relayout for add module |  | 50 | Box Main 3 ( Plant B )
[8 empty] | Freezer pass time |  | 43.0 min | time |  | 2 | Word
[8 empty] | Cooling pass time |  | 38.1 min | time |  | 2 | Word
[8 empty] | Fan speed select |  | High,Mid,Low | - |  | 1 | Bit
[8 empty] | Status massage |  | Cooling | - |  | 1 | Word
[8 empty] | CIP Select |  | Light washing,Full washing,Feeding Finish | - |  | 1 | Word
[8 empty] | Inlet balance fan |  | 50.00 Hz |  |  | 2 | Word
[8 empty] | In-peration |  | - | Operation time |  | 1 | Bit
[8 empty] | Auto running |  | - | Operation time |  | 1 | Bit
[8 empty] | Stopping |  | - | stopping Time |  | 1 | Bit
[8 empty] | Emergency stop |  | - | Stopping Time |  | 1 | Bit
[8 empty] | Reserve |  |  |  |  | 35
7 | 4 | B | 2 | Clean room | Vertical Packing | Micro controller |  | Auto running | On,Off |  | Operation time | 1 |  | Digital Input | I/O Link |  | Add relay for tab signal,Re layout | 3 |  | Box Main 4 ( Plant B )
[8 empty] | Stop | On,Off |  | stopping Time | 1
[8 empty] | Emergency stop | On,Off |  | stopping Time | 1
8 | 4 | B | 2 | Clean room | General Packer | CJ2M CPU12 | MONITOUCH G10 | Auto running | On,Off |  | Operation time | 1 |  | Digital Input | I/O Link |  | Add relay for tab signal,Re layout | 3 |  | Box Main 4 ( Plant B )
[8 empty] | Stop | On,Off |  | stopping Time | 1
[8 empty] | Emergency stop | On,Off |  | stopping Time | 1
10

## Equipment
Summarize
| No. | Model | Name | Supplier | Brand | Unit price | Quantity | Total (THB) | Installation point
| 1 | Summarize Plant A |  |  |  | 609390 | 1 | 609390 | Control Box and Equipment
| 2 | Summarize Plant B |  |  |  | 411198 | 1 | 411198 | Control Box and Equipment
| 2 | Summarize Equipment Master controller |  |  |  | 14430 | 1 | 14430 | Control Box and Equipment
| Summarize total | [6 empty] | 1020588
Equipment Master Controller
| No. | Model | Name | Supplier | Brand | Unit Price | Quantity | Total (THB)
| 1 | KV-8000 | PLC |  | KEYENCE |  | 1 | 0 | Quote from Keyence
| 2 | KV-XLE02 | LINK PLC I/E |  | KEYENCE |  | 1 | 0 | Quote from Keyence
| 3 | KV-XD02 | Data Utilisation Unit |  | KEYENCE |  | 1 | 0 | Quote from Keyence
| 4 | KVM-16G | MEMORY CRAD 16 GB |  | KEYENCE |  | 1 | 0 | Quote from Keyence
| 5 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300
| 6 | OAM-60000-45-5GT | SWITCHING HUB | Data Automation | OAM Link | 1985 | 1 | 1985
| 7 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165
| 8 | - | Terminal End Plate Stopper DIN Rail ( 1 Pack/ 10 Pcs.) | PT Automation | IDEC | 50 | 1 | 50
| 9 | BNDH15W | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 1 | 1830
| 10 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 1 | 100
| 11 |  |  |  |  | 0 | 1 | 0
| 12 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000
14430
Equipment Keyence summarize
| 1 | KV-EP02 | Remote I/O Module |  | KEYENCE |  | 5 | 0
| 2 | NC-32EX | Input unit |  | KEYENCE |  | 8 | 0
| 3 | NC-16EX | Input unit |  | KEYENCE |  | 3 | 0
PLANT A | Box Main 2 ( Collect Prepare for fry )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 16000 | 1 | 16000 | Prepare for fry
| 2 | OAM-60000-45-8Txm ( 8 Port ) | SWITCHING HUB | Data Automation | OAM Link | 2340 | 1 | 2340 | Prepare for fry
| 3 | FX3U-ENET-L | Module Ethernet mitsubishi | DHOWA |  | 12000 | 4 | 48000 | Prepare for fry use for New Hicook
| 4 |  | Cable Expiantion 0.5M for Ethernet module | DHOWA |  | 2000 | 4 | 8000 | Prepare for fry use for New Hicook
| 5 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Prepare for fry
| 6 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Prepare for fry
| 7 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Prepare for fry
| 8 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Prepare for fry
| 9 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Prepare for fry
| 10 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 10 | 100 | Prepare for fry
| 11 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 1 | 1830 | Prepare for fry
| 12 |  | Name plate | - | - | 500 | 1 | 500 | Prepare for fry
| 13 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Prepare for fry
| 14 |  | Labor cost connect to machine | PLC Center |  | 10000 | 4 | 40000 | Prepare for fry
| 15 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Prepare for fry
| 16 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Prepare for fry
160860
Slave Box 2-1 ( Collect KOPPEN FRYER )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 14000 | 1 | 14000 | Koppen fryer
| 2 | KV-EP02 | Remote I/O Module |  | KEYENCE |  | 1 | 0 | Koppen fryer
| 3 | NC-32EX | Input unit |  | KEYENCE |  | 1 | 0 | Koppen fryer
| 4 | NC-16EX | Input unit |  | KEYENCE |  | 1 | 0 | Koppen fryer
| 5 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Koppen fryer
| 6 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Koppen fryer
| 7 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Koppen fryer
| 8 | G2R-1-SN-220VAC | Relay | AutomationCad | OMRON | 500 | 32 | 16000 | Koppen fryer
| 9 | P2RF-05-E | SOCKET RELAY OMRON | AutomationCad | OMRON | 180 | 32 | 5760 | Koppen fryer
| 10 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Koppen fryer
| 11 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Koppen fryer
| 12 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 10 | 100 | Koppen fryer
| 13 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 2 | 3660 | Koppen fryer
| 14 |  | Name plate | - | - | 500 | 1 | 500 | Koppen fryer
| 15 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Koppen fryer
| 16 |  | Labor cost connect to machine | PLC Center |  | 10000 | 1 | 10000 | Koppen fryer
| 17 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Koppen fryer
| 18 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Koppen fryer
94110
Slave Box 2-2 ( Collect Steam cook )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 14000 | 1 | 14000 | Koppen fryer
| 2 | KV-EP02 | Remote I/O Module |  | KEYENCE |  | 1 | 0 | Koppen fryer
| 3 | NC-32EX | Input unit |  | KEYENCE |  | 1 | 0 | Koppen fryer
| 4 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Koppen fryer
| 5 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Koppen fryer
| 6 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Koppen fryer
| 7 | G2R-1-SN-220VAC | Relay | AutomationCad | OMRON | 500 | 20 | 10000 | Koppen fryer
| 8 | P2RF-05-E | SOCKET RELAY OMRON | AutomationCad | OMRON | 180 | 20 | 3600 | Koppen fryer
| 9 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Koppen fryer
| 10 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Koppen fryer
| 11 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 10 | 100 | Koppen fryer
| 12 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 2 | 3660 | Koppen fryer
| 13 |  | Name plate | - | - | 500 | 1 | 500 | Koppen fryer
| 14 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Koppen fryer
| 15 |  | Labor cost connect to machine | PLC Center |  | 10000 | 1 | 10000 | Koppen fryer
| 16 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Koppen fryer
| 17 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Koppen fryer
85950
Box Main 3 ( Collect spiral 2,3,6,7 )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 16000 | 1 | 16000 | Spiral room Main
| 2 | QJ71EN71-100 | Module Ethernet Mitsubishi | Nort Tech | MITSUBISHI | 23000 | 2 | 46000 | Spiral 6,7
| 3 | KV-EP02 | Remote I/O Module |  | KEYENCE |  | 1 | 0 | Spiral room Main
| 4 | NC-32EX | Input unit |  | KEYENCE |  | 2 | 0 | Spiral room Main
| 5 | NC-16EX | Input unit |  | KEYENCE |  | 1 | 0 | Spiral room Main
| 6 | OAM-60000-45-5GT | SWITCHING HUB | Data Automation | OAM Link | 1985 | 1 | 1985 | Spiral room Main
| 7 | G2R-1-SN-220VAC | Relay | AutomationCad | OMRON | 500 | 60 | 30000 | Spiral room Main
| 8 | P2RF-05-E | SOCKET RELAY OMRON | AutomationCad | OMRON | 180 | 60 | 10800 | Spiral room Main
| 9 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Spiral room Main
| 10 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Spiral room Main
| 11 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Spiral room Main
| 12 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Spiral room Main
| 13 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Spiral room Main
| 14 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 10 | 100 | Spiral room Main
| 15 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 3 | 5490 | Spiral room Main
| 16 |  | Name plate | - | - | 500 | 1 | 500 | Spiral room Main
| 17 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Spiral room Main
| 18 |  | Labor connect to machine | PLC Center |  | 10000 | 4 | 40000 | Spiral room Main
| 19 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Spiral room Main
| 20 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Spiral room Main
194965
Box Main 4 ( Collect Polystar 1-3 )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 10000 | 1 | 10000 | Polystar room
| 2 | OAM-60000-45-5GT | SWITCHING HUB | Data Automation | OAM Link | 1985 | 1 | 1985 | Polystar room
| 3 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Polystar room
| 4 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Polystar room
| 5 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Polystar room
| 6 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Polystar room
| 7 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 2 | 200 | Polystar room
| 8 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 10 | 100 | Polystar room
| 9 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 1 | 1830 | Polystar room
| 10 |  | Name plate | - | - | 500 | 1 | 500 | Polystar room
| 11 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Polystar room
| 12 |  | Labor cost connect to machine | PLC Center | - | 5000 | 3 | 15000 | Polystar room
| 13 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Polystar room
| 14 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Polystar room
73505
Summarize Plant A |  |  | 609390 | Bath
PLANT B | Box Main 2 ( Collect Fry Fry )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 16000 | 1 | 16000 | Fry Fry Room
| 2 | KV-EP02 | Remote I/O Module |  | KEYENCE |  | 1 | 0 | Fry Fry Room
| 3 | NC-32EX | Input unit |  | KEYENCE |  | 1 | 0 | Fry Fry Room
| 4 | NC-16EX | Input unit |  | KEYENCE |  | 1 | 0 | Fry Fry Room
| 5 | FX3U-ENET-L | Module Ethernet mitsubishi | DHOWA |  | 12000 | 3 | 36000 | Fry Fry Room
| 6 |  | Cable Expiantion 0.5M for Ethernet module | DHOWA |  | 2000 | 3 | 6000 | Fry Fry Room
| 7 | OAM-60000-45-8Txm ( 8 Port ) | SWITCHING HUB | Data Automation | OAM Link | 2340 | 1 | 2340 | Fry Fry Room
| 8 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Fry Fry Room
| 9 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Fry Fry Room
| 10 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Fry Fry Room
| 11 | G2R-1-SN-220VAC | Relay | AutomationCad | OMRON | 500 | 35 | 17500 | Fry Fry Room
| 12 | P2RF-05-E | SOCKET RELAY OMRON | AutomationCad | OMRON | 180 | 35 | 6300 | Fry Fry Room
| 13 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 5 | 500 | Fry Fry Room
| 14 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 5 | 500 | Fry Fry Room
| 15 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 10 | 100 | Fry Fry Room
| 16 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 3 | 5490 | Fry Fry Room
| 17 |  | Name plate | - | - | 500 | 1 | 500 | Fry Fry Room
| 18 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Fry Fry Room
| 19 |  | Labor cost connect to machine and config module Ethernet | PLC Center | - | 10000 | 4 | 40000 | Fry Fry Room
| 20 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Fry Fry Room
| 21 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Fry Fry Room
174920
Box Main 3 ( Collect Spiral 4,5 )
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 10000 | 1 | 10000 | Spiral room
| 2 | FX3U-ENET-L | Module Ethernet mitsubishi | DHOWA |  | 12000 | 2 | 24000 | Spiral room
| 3 |  | Cable Expiantion 0.5M for Ethernet module | DHOWA |  | 2000 | 2 | 4000 | Spiral room
| 4 | OAM-60000-45-5GT | SWITCHING HUB | Data Automation | OAM Link | 1985 | 1 | 1985 | Spiral room
| 5 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Spiral room
| 6 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Spiral room
| 7 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Spiral room
| 8 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 1 | 100 | Spiral room
| 9 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 1 | 100 | Spiral room
| 10 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 6 | 60 | Spiral room
| 11 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 1 | 1830 | Spiral room
| 12 |  | Name plate | - | - | 500 | 1 | 500 | Spiral room
| 13 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 2 | 18 | Spiral room
| 14 |  | Labor cost connect to machine and config module Ethernet | PLC Center | - | 10000 | 2 | 20000 | Spiral room
| 15 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Spiral room
| 16 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Spiral room
106193
Box Main 3 ( Collect Clean room)
| 1 | RBC-09 W450 x H600 x D250 mm. | Control Box ( SUS304 ) | RBC | - | 16000 | 1 | 16000 | Clean room
| 2 | KV-EP02 | Remote I/O Module |  | KEYENCE |  | 1 | 0 | Clean room
| 3 | NC-32EX | Input unit |  | KEYENCE |  | 2 | 0 | Clean room
| 5 | OAM-60000-45-5GT | SWITCHING HUB | Data Automation | OAM Link | 1985 | 1 | 1985 | Clean room
| 6 | NV63-CV 2P-15A | ELCB | Nort Tech | MITSUBISHI | 3135 | 1 | 3135 | Clean room
| 7 | CP30-BA-2P-5A | Circuit Protector | - | MITSUBISHI | 2165 | 1 | 2165 | Clean room
| 8 | S8VK-G12024 | Switching Power Supply | AutomationCad | OMRON | 3300 | 1 | 3300 | Clean room
| 9 | G2R-1-SN-220VAC | Relay | AutomationCad | OMRON | 500 | 32 | 16000 | Clean room
| 10 | P2RF-05-E | SOCKET RELAY OMRON | AutomationCad | OMRON | 180 | 32 | 5760 | Clean room
| 11 | DNR314-100 | Din rail | Hardwarehouse | Hardwarehouse | 100 | 3 | 300 | Clean room
| 12 | WD4030 PRI | Wire duct (WD) | Hardwarehouse | Hardwarehouse | 100 | 3 | 300 | Clean room
| 13 | G6D-4-SB | Short Bar | PT Automation | OMRON | 10 | 6 | 60 | Clean room
| 14 |  | Terminal IDEC ( 1 Box / 25 Pcs.) | Hardwarehouse | IDEC | 1830 | 3 | 5490 | Clean room
| 15 |  | Name plate | - | - | 500 | 1 | 500 | Clean room
| 16 |  | End plate terminal | Hardwarehouse | IDEC | 9 | 10 | 90 | Clean room
| 17 |  | Labor cost connect to machine and config module Ethernet | PLC Center | - | 10000 | 4 | 40000 | Clean room
| 18 |  | Accessory installation box |  |  | 30000 | 1 | 30000 | Clean room
| 19 |  | Other equipment of wiring. | - | - | 5000 | 1 | 5000 | Clean room
130085
Summarize Plant B |  |  | 411198 | Bath

## Estimate cost
Machine operation monitoring system | Man power 1 person |  |  | Location | Remark
Make program for Collection data form machine |  | 20 | day | office
Make dashboard for monitor |  | 10 | day | office
Wiring Box control |  | 10 | day | office
Install Program and Config system |  | 7 | day | out site
Re-Wiring control box from machine and Recheck signal | 1 Day/Machine | 20 | day | out site | Re-layout 24 machine and add relay,Module Ethernet
Paramiter setting | 1 Day/Machine | 10 | day | out site | Case addition FX3U/FX3G-ETHERNET
test and confrim |  | 13 | day | out site
SUM |  | 90 | day