## Slide 1
Machine operation monitoring system specifications
Documentation EN Blueprint for TNF
Blueprint
R2
Made for: Thai Nippon food co. Ltd.
By: TOMAS TECH CO.,LTD.
Version 01/Nov/2023
Confidential

## Slide 2
Revision History
Date | Version | File name | Details
02/Oct/2023 | R1 | Machine operation monitoring system specifications Documentation EN Blueprint for TNF Blueprint R1 | First edition
01/Nov/2023 | R2 | Machine operation monitoring system specifications Documentation EN Blueprint for TNF Blueprint R2 | Second edition

## Slide 3
■Contents
1. Overview
2. Overall configuration diagram
3. Install TB-BOX
4. Hardware install
5. IP Assign
6. Cable specifications
7. Q&A
8. Sign off

## Slide 4
1. Overview
It is a system that retrieves data from machines within Plant A and Plant B within the
Thai Nippon food factory in the form of I/O signal and Ethernet. The data is displayed and stored.

## Slide 5
2. Overall configuration diagram
Overall configuration diagram (Hardware configuration)
# | Item | Qty | IP Address | Preparation By
1 | Server PC for Record data window server | 1 |  | TNF
2 | PLC Keyence KV-8000 | 1 | 192.168.XXX.1 | TNF
3 | KV-XLE02 | 1 | 192.168.XXX.2 | TNF
4 | KV-XD02 | 1 | 192.168.XXX.4 | TNF
5 | KVM-16G | 2 |  | TNF
6 | KV-EP02 | 5 | 192.168.XXX.20-30 | TNF
7 | NC-32EX | 8 |  | TNF
8 | NC-16EX | 3 |  | TNF
9 | Ethernet module ( FX3U-ENET-L) | 10 | 192.168.XXX.50-69 | Tomas
10 | Cable Expiation 0.65M for Ethernet module | 10 |  | Tomas
11 | Ethernet module (QJ71EN71-100) | 2 | 192.168.XXX.70-80 | Tomas
12 | AMX-PLC | 3 | 192.168.XXX.40-49 | Tomas
13 | Ethernet hub | 10 |  | Tomas
14 | Terminal Box | 4 |  | Tomas
Server room
TNF
server
Client pc
Prepare by TNF
Prepare by Tomas
Control Box in server room
PLC Keyence
HUB
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Wiring
Monitoring
Plant A
Plant B
Switching
Hub 1
Switching
Hub 2
Switching
Hub 1
Switching
Hub 2
TB Box 1
TB Box 2
TB Box 1
TB Box 2
14 Machine
10 Machine

## Slide 6
2. Overall configuration diagram
Overall configuration diagram (Hardware configuration)
Prepare by TNF
Prepare by Tomas
Control Box in server room
PLC Keyence
HUB
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
Monitoring
TB Box 1
Switching
Hub 1
Server room
Plant A
Main Breaker
TB Box 2
Switching
Hub 2
Main Breaker
High cook New 1
High cook New 2
High cook 1
High cook 1
Sun max
Steam cook
Koppen fryer
Spiral No.6
Spiral No.7
Poly Star 1
Poly Star 2
Poly Star 3
Spiral No.2
Spiral No.3

## Slide 7
2. Overall configuration diagram
Overall configuration diagram (Hardware configuration)
Prepare by TNF
Prepare by Tomas
Control Box in server room
PLC Keyence
HUB
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
Monitoring
TB Box 1
Switching
Hub 1
Server room
Plant B
Main Breaker
TB Box 2
Switching
Hub 2
Main Breaker
Fryer 1
Fryer 2
Stream Oven 1
Koppen Fryer
Spiral No.4
Spiral No.5
General Pack 1
General Pack 2
Vertical Pack 1
Vertical Pack 2

## Slide 8
2. Overall configuration diagram
TB Box install ( Hardware install )
*Hub cabinet location in Plant A
TB Box 1
TB Box 2

## Slide 9
2. Overall configuration diagram
TB Box install ( Hardware install )
TB Box 1
Plant A ( C5 Zone )
TB Box 2
High cook New 1
High cook New 2
High cook 1
High cook 1
Sun max
Steam cook 1
Koppen fryer
Spiral No.6
Spiral No.7
Poly Star 1
Poly Star 2
Poly Star 3
Spiral No.2
Spiral No.3
C5 Hub cabinet
Main Breaker
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
Prepare by TNF
Prepare by Tomas
Plant A ( C4 Zone )
C4 Hub cabinet
Main Breaker
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
Prepare by TNF
Prepare by Tomas
Lan cable [machine <> TB1] = 5 Cable
Lan cable [TB1 <> C5] = 1 Cable
AC 220 V Cable Main [CB <> TB1] = 1 Set
I/O Signal Cable [TB1 <> MC] = 4 Cable
Lan cable [machine <> TB2] = 5 Cable
Lan cable [TB2 <> C4] = 1 Cable
AC 220 V Cable Main [CB <> TB2] = 1 Set
I/O Signal Cable [TB2 <> MC] = 4 Cable
*I/O Cable 18G x 0.75 = 2/Machine
*I/O Cable 18G x 0.75 = 2/Machine

## Slide 10
2. Overall configuration diagram
TB Box install ( Hardware install )
*Hub cabinet location in Plant B
TB Box 1
TB Box 2
Cabinet name ???
Cooking Zone
Cabinet name ???
Packing Zone

## Slide 11
2. Overall configuration diagram
Overall configuration diagram (Hardware configuration)
TB Box 2
Spiral No.4
Spiral No.5
General Pack 1
General Pack 2
Vertical Pack 1
Vertical Pack 2
Plant B ( Cooking Zone )
Plant B ( Packing Zone )
TB Box 1
Fryer 1 Hi-Cook
Fryer 2 Hi-Cook
Stream Oven 1
Koppen Fryer
Hub cabinet
Main Breaker
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
Prepare by TNF
Prepare by Tomas
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
Prepare by TNF
Prepare by Tomas
Hub cabinet
Main Breaker
Lan cable [Machine <> TB1] = 3 Cable
Lan cable [TB1 <> C4] = 1 Cable
AC 220 V Cable Main [CB <> TB1] = 1 Set
I/O Cable [TB1 <> MC] = 2 Cable
Lan cable [Machine <> TB2] = 2 Cable
Lan cable [TB2 <> C4] = 1 Cable
AC 220 V Cable Main [CB <> TB2] = 1 Set
I/O Cable [TB2 <> MC] = 4 Cable
*I/O Cable 18G x 0.75 = 2/Machine
*I/O Cable 18G x 0.75 = 1/Machine

## Slide 12
3. TB-BOX Installation
C5 Hub cabinet
Installation box Type 1
C5 Hub cabinet
TB Box 1
Air blow
Prepare by TNF
Prepare by Tomas
Fan
footpath
Main breaker
Enclosure Box
800 x 600 x 250
Mounting
footpath
TB Box 1

## Slide 13
3. TB-BOX Installation
Hub cabinet
Installation box Type 2
C5 Hub cabinet
TB Box 1
Prepare by TNF
Prepare by Tomas
Fan
footpath
Enclosure Box
800 x 600 x 250
Mounting
footpath
TB Box 1

## Slide 14
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C5 Zone ) New High-cook 1
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
FX3U-ENET-L
High cook New 1
Add new
*Install the FX3U-ENET-L device for retrieving data from the New High-cook machine.

## Slide 15
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C5 Zone ) New High-cook 2
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
FX3U-ENET-L
High cook New 2
Add new
*Install the FX3U-ENET-L device for retrieving data from the New High-cook2 machine.

## Slide 16
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C5 Zone ) Sun Max
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
FX3U-ENET-L
Sun Max
Add new
**Change the layout by moving the marked devices closer together so that the FX3U-ENET-L can be installed.

## Slide 17
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C5 Zone ) Koppen fryer
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
KV-EP02
Koppen fryer
Add new
*Attach Din-rial to number 1 to install Terminal for retrieving data from I/O machines.
1
KV-EP02

## Slide 18
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C5 Zone ) Steam cook 1
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
KV-EP02
Steam cook 1
Add new
**Change the layout by moving the marked devices closer together so that the terminal can be installed.
1

## Slide 19
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C4 Zone ) Spiral No.2 , No.3
TB Box 2
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
KV-EP02
Spiral No.2
Add new
1. Attach Din-rial to number 1 to install Terminal for retrieving data from I/O machines.
2. Install a wire duct for storing wires at the signal tab from the machine.
KV-EP02
1
2
Spiral No.3

## Slide 20
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C4 Zone ) Spiral No.2 , No.3
TB Box 3
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
QJ71E7-100
Spiral No.6
Add new
*Install the QJ71E71-100 device for retrieving data from the New High-cook machine.
Spiral No.7
QJ71E7-100

## Slide 21
4. Hardware install
Installation of equipment for extracting data from machines
Plant A ( C4 Zone ) Poly star 1,2,3
TB Box 2
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
AMX PLC
Poly star 1
Add new
*Install AMX-PLC for retrieving data from the GOT2000 screen to send data to the Main PLC.
Poly star 3
Poly star 2

## Slide 22
4. Hardware install
Installation of equipment for extracting data from machines
Plant B ( Cooking Zone ) High-cook 1,2
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
FX3U-ENET-L
High cook 1,2
Add new
*Install the FX3U-ENET-L device for retrieving data from the High-cook machine.

## Slide 23
4. Hardware install
Installation of equipment for extracting data from machines
Plant B ( Cooking Zone ) Steam Oven 1
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
FX3U-ENET-L
Stream Oven 1
Add new
The installation of the equipment cannot be verified because the control cabinet cannot be opened.

## Slide 24
4. Hardware install
Installation of equipment for extracting data from machines
Plant B ( Cooking Zone ) Koppen fryer
TB Box 1
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
KV-EP02
Koppen fryer
Add new
*Attach Din-rial to number 1 to install Terminal for retrieving data from I/O machines.
KV-EP02
1

## Slide 25
4. Hardware install
Installation of equipment for extracting data from machines
Plant B ( Packing Zone ) Spiral No.4 , No.5
TB Box 2
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
FX3U-ENET-L
Spiral No.4
Add new
**Change the layout by moving the marked devices closer together so that the FX3U-ENET-L can be installed.
Spiral No.5
FX3U-ENET-L

## Slide 26
4. Hardware install
Installation of equipment for extracting data from machines
Plant B ( Packing Zone ) General pack 1,2
TB Box 2
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
KV-EP02
General Pack 1,2
Add new
*Attach Terminal for retrieving data from I/O machines.
KV-EP02

## Slide 27
4. Hardware install
Installation of equipment for extracting data from machines
Plant B ( Packing Zone ) Vertical pack 1,2
TB Box 2
PLC Keyence
XLE-02
DC 24 V Cable
AC 220 V Cable
Ethernet Lan cable
I/O Cable
KV-EP02
Vertical Pack 1,2
Add new
*Install EP02 in box Vertical pack machine
KV-EP02

## Slide 28
5. IP Assign
Assigning IP for use in the Machine operation monitoring system
Plant | No. | Equipment Name | IP Assign | Use in
A | 1 | PLC KV-8000 | XXX.XXX.XXX.1 | Main system
A | 2 | KV-XLE02 (Port 1) | XXX.XXX.XXX.2 | Main system
A | 3 | KV-XLE02 (Port 2) | XXX.XXX.XXX.3 | Main system
A | 4 | KV-XD02 (Port 1) | XXX.XXX.XXX.4 | Main system
A | 5 | KV-XD02 (Port 2) | XXX.XXX.XXX.5 | Main system
A | 6 | KV-EP02 | XXX.XXX.XXX.20 | Control system ( TB1 Plant A )
A | 7 | KV-EP02 | XXX.XXX.XXX.21 | Control system ( TB2 Plant A )
B | 8 | KV-EP02 | XXX.XXX.XXX.22 | Control system ( TB1 Plant B )
B | 9 | KV-EP02 | XXX.XXX.XXX.23 | Control system ( TB1-1 Plant B )
B | 10 | KV-EP02 | XXX.XXX.XXX.24 | Control system ( TB1-2 Plant B )
A | 11 | AMX-PLC | XXX.XXX.XXX.40 | Control system ( Polystar 1 )
A | 12 | AMX-PLC | XXX.XXX.XXX.41 | Control system ( Polystar 2 )
A | 13 | AMX-PLC | XXX.XXX.XXX.42 | Control system ( Polystar 3 )
A | 14 | FX3U-ENET-L | XXX.XXX.XXX.50 | High-cook1
A | 15 | FX3U-ENET-L | XXX.XXX.XXX.51 | High-cook2
A | 16 | FX3U-ENET-L | XXX.XXX.XXX.52 | New High-cook1
A | 17 | FX3U-ENET-L | XXX.XXX.XXX.53 | New High-cook2
A | 18 | FX3U-ENET-L | XXX.XXX.XXX.54 | Sunmax
B | 19 | FX3U-ENET-L | XXX.XXX.XXX.55 | High-cook1
B | 20 | FX3U-ENET-L | XXX.XXX.XXX.56 | High-cook2
B | 21 | FX3U-ENET-L | XXX.XXX.XXX.57 | Steam Oven1
B | 22 | FX3U-ENET-L | XXX.XXX.XXX.58 | Spiral No.3
B | 23 | FX3U-ENET-L | XXX.XXX.XXX.59 | Spiral No.4
A | 24 | QJ71EN71-100 | XXX.XXX.XXX.70 | Spiral No.6
A | 25 | QJ71EN71-100 | XXX.XXX.XXX.71 | Spiral No.7
 | 26 |  | XXX.XXX.XXX.100-150 | For Spare
 | 27 |  | XXX.XXX.XXX.100-150 | For Service
 | 28 |  | XXX.XXX.XXX.200-254 | For monitoring

## Slide 29
6. Cable specifications
Signal I/O *By owner
Part no.10047 18G x 0.75

## Slide 30
7. Q&A

## Slide 31
8. Sign off
We hereby acknowledge and agree the above-mentioned blueprint requirements.
Any changes required after the sign off for this blueprint will be addressed through the change request process.
Thai Nippon Foods Co., Ltd.
Sign:
## END OF BLUEPRINT##
Name:
Title:
Date:
TOMAS TECH CO.,LTD.
Sign:
Name:
Title:
Date: